## Slide 1: LED Lighting Interference Examples
Andrew Roy and Gregory Baker

## Slide 2: Scope
LED interference at KMKE – 2015-2017
LED interference at KBNA – 2016
LED interference conclusions

## Slide 3: LED Interference at KMKE - 2017
Inconsistent “No Comm.” on ACARS at Gate 51 – Nov. 2015
  Initially believed to be a coverage issue
  Repositioned antenna, still had same issues
Realized Interference localized to 1 Gate – Mar. 2016
  Noise floor -90 dBm ±5 dB around Jetway
  Assumed to be electrical noise

## Slide 4: Troubleshooting Steps
Initial suspect was Ground Power Unit (GPU)
Performed test have aircraft powered using APU instead of GPU
  Marginally improved VDL performance at gate…
  …but didn’t eliminate issue
Flights diverted to adjacent gate 53
  No issues reported
  Confirmed localized to gate 51

## Slide 5: LED Interference at MKE
Suspected LED interference from reports received
  Service provider, ASRI and US regulator on-site to find and identify
2 LED Sources raising noise floor on ramp
  #1 has Line of Sight through windows to ramp
    LED retrofit by bathroom
  #2 close to windows, line of sight to ramp
    LED track lighting by accessory store
  Source #2 emissions not as strong as source #1
On/Off Testing Performed
  Need to coordinate with various owners
  Verified noise below jetway and on ramp after both sources turned off

## Slide 6: Locations
Gate 51 Gate 53

## Slide 7: Gate D51

## Slide 8: Source #1 from Gate D51
LED Source #1
Gate 53

## Slide 9: Source #2 – View towards gate D51
D51
LED Source #2

## Slide 10: Source #2 Store Entrance

## Slide 11: Line of Sight Video

## Slide 12: LED Source #1

## Slide 13: Direction Finding

## Slide 14: KMKE Resolution
Replaced LED Source #1
LED source #2 left on to see if power levels high enough to still affect aircraft when next at gate
  If it is still there:
    Interim solution: airport planning to have the store turn off track lighting when plane is near or at gate
    Long-term solution: replace lighting with different type
  No interference reported as of Aug 2017
LED interference seen from interior sources
  Commercial/residential equipment
Multiple sources of interference complicated identification
  Low power broadband noise difficult to direction find

## Slide 15: LED Interference at KBNA – 2016
Information courtesy of ARINC/Rockwell Collins
Airline Report: ACARS & VDL poor and nocomms at two (9 & 25) airport gates
Initial Actions:
  Verified ground station functionality.
  On-site station inspection of transceiver, coax, antenna, and availability of RF signal
  All good; problems persist.
2nd Actions: revisit station, replace transceiver and related
  Problems persist
3rd: Engineering (vs. Field) staff & test equipment from HQ re-visit KBNA

## Slide 16: Engineering Review of KBNA
Careful assessment of the RF environment at KBNA
Test Equipment:
  R8000B communications system analyzer (Setting: 25kHz BW, ~100Hz RBW)
  RC/IMS developed tools to measure background noise relative to signal strength
  Handheld retractable antenna
Noise Source is Isolated to Jetway
  LEDs: External Jetway Lighting

## Slide 17: Test Antenna at Jetway & LED Lights

## Slide 18: Analyzer Display: LEDs ON - Wideband Noise

## Slide 19: Analyzer Display: LEDs OFF: Background Noise is Reduced by 40dB

## Slide 20: KBNA Resolution
Airport had been encouraged to move toward LED lighting for efficiency
  Lights were replaced with CFLs
Post event review highlighted that interference was only happening when dark

## Slide 21: LED Interference Conclusions
Actual LED not the problem, but the power regulator
  30 to 300 MHz band particularly susceptible
Low power/close proximity interference can be hard to direction find
  How to differentiate between other noise sources
  Detection equipment may not be suitable to signal type
Lack of experience with newer technology for field personnel
  Often requires knowledgeable personnel with suitable equipment onsite to find and identify
How much does it cost to change a light bulb?
  Identification, localization, tracking, analysis, …
  Interference maybe from equipment that cannot be turned off without coordination
  Need an aircraft in place to fully test resolution
Buyers/suppliers of airport lighting not always aware of the RF issues
  May not be part of the aviation industry
  Focus on price rather than RF performance

## Slide 22: Questions?